## Information
Although a similar concept to insulating hot water pipes in your home, the higher operating temperatures and volumes used in manufacturing industries can translate into much quicker payback times. Heat losses in steam or hot water reticulation systems are not generally a pressing production need - but over a year their contribution to a plant's operating costs can be quite signficant. The savings from reducing heat loss go straight onto the bottom line.
The pipework heat loss calculator is designed to help identify opportunities for improvement. It is not intended as a detailed design tool and should not be used as such. If, by using the calculator, you are made aware of an area where improvements may yield savings in costs, energy and greenhouse gas emissions and this sparks further investigation, then the tool has been used appropriately. We would expect and recommend that, particularly where the scale of the capital expenditure and process changes required are signficant, that you seek competent expert assistance to confirm the value of any proposed changes.
The calculator compares the heat loss from an uninsulated and insulated section of pipe and provides an estimate of the cost benefit. Because the rate of heat loss is different from vertical and horizontal pipes, you are asked to enter the estimated length of both respectively.
Other important factors necessary to calculate heat loss are the temperature of the fluid being distributed and the ambient environment adjacent to the pipe respectively. You are also prompted to enter a proposed insulation thickness. To reduce data input, the insulate is based on a typical fibreglass based product.
Finally, in order to calculate daily and annual operating costs, daily operating hours and operating days per year together with fuel type and cost are entered. Entering an estimated boiler efficiency allows an estimate of the actual fuel saving (rather than just the energy saving at the point of use) form improving insulation.
The heat loss is estimated using equations that account for conduction for the insulated pipe and radiation and convection for the uninsulated tank.

## Calculator
Heat loss from a pipe
Schedule 40 pipe data
Nominal pipe diameter, mm | [8 empty] | m | ft |  |  |  | 9 |  | Nominal diam (mm) | External area (m2/m) | OD (mm)
[5 empty] | 10 |  |  | Outside diameter | 0.27305 | 10 |  | 10 |  | 14 | 1 | 15 | 0.067029 | 21.336
Vertical length, m | 16 | [12 empty] | 14 | 2 | 20 | 0.083786 | 26.67
Horizontal length, m | 41 | [6 empty] | Vertical length, ft | 52.4934 |  |  |  |  | 273.05 | 3 | 25 | 0.10533 | 33.528
[8 empty] | Horizontal length, ft | 134.5144 | [5 empty] | 4 | 32 | 0.13246 | 42.164
Insulation thickness (mm) | 25 | [7 empty] | m2/m | ft2/ft |  |  |  |  | 5 | 40 | 0.15161 | 48.26
[8 empty] | Area/linear length | 14 | 31.4159 |  |  |  |  | 6 | 50 | 0.18992 | 60.452
Fluid temperature, C | 185 | [7 empty] | F | R |  |  |  |  | 7 | 60 | 0.22981 | 73.152
Ambient temperature, C | 12 | [7 empty] | 365 | 824.67 |  |  |  |  | 8 | 80 | 0.27929 | 88.9
|  |  |  | 1 |  |  |  |  | 53.6 | 513.27 |  |  |  |  | 9 | 90 | 0.31919 | 101.6
Operating hours | [14 empty] | 10 | 100 | 0.35908 | 114.3
Hours per day | 18 | [6 empty] | Insulated pipe | [6 empty] | 11 | 125 | 0.44367 | 141.224
Days per year | 220 | [6 empty] | Thermal conductivity, fibreglass | 0.04125 | W/m/C |  | See pipe insulation PDF giving 0.286 BTU in/ft2/hr/F. |  |  | 12 | 150 | 0.52905 | 168.402
[9 empty] | m | ft |  |  |  |  | 13 | 200 | 0.68864 | 219.202
Fuel type | [7 empty] | Insulation thickness | 0.025 | 0.082021 |  |  |  |  | 14 | 250 | 0.85781 | 273.05
Diesel | [7 empty] | Insulation diameter | 0.32305 | 1.0599 |  |  |  |  | 15 | 300 | 1.0174 | 323.85
LFO (light fuel oil) | [8 empty] | C | F | R |  |  |  | 16 | 325 | 1.1172 | 355.6
LPG |  |  |  | 1 |  | 1 | Insulation surface temp |  | 17.7792 | 64.0025 | 523.6725 |  |  |  | 17 | 375 | 1.2767 | 406.4 | 5
Coal | [8 empty] | 5.5691 | [5 empty] | 18 | 425 | 1.4363 | 457.2
Electricity | [6 empty] | Surface coefficent, ha (estimated as mean hc +hr) | Trial & error | 543.089 | W/m2 C |  |  |  |  | 19 | 475 | 1.5959 | 508
[8 empty] | Pipe heat loss, kW/m | 0.1158 | kW/m | (Kern, p19) |  |  |  | 20 | 575 | 1.9151 | 609.6
Fuel cost, $/tonne | 100 | [6 empty] | Check insulation resistance | 12.2101 | C |  |  | Fuel type control | 4
Heat raising efficiency | 65%
[8 empty] | No insulation: assume convection and radiation primary resistance | [5 empty] | NCV
[8 empty] | Convection | HTC, BTU/hr ft2 F | HTC, W/m2 C
| Daily energy waste, kWh/day | Daily energy waste cost, $/day | Annual energy waste cost, $/year |  |  |  |  | Horizontal pipes | 1.1811 | 6.7067 | (ref Kern p215) |  | Diesel (MJ/l) | 35.8
Uninsulated pipe | 115306.1006 | 3756.5788 | 826447.3452 |  |  |  |  | Vertical pipes | 0.94491 | 5.3654 |  |  | LFO (MJ/l) | 37.9
Insulated pipe | 118.8062 | 3.8706 | 851.5343 | [5 empty] | Heat loss BTU/ft | Heat loss kW/m |  |  | LPG (MJ/kg) | 46
Potential annual saving |  |  | 825595.8109 |  |  |  |  | Horizontal pipes | 11554.9518 | 16.2437 |  |  | Coal (MJ/kg) | 17
[8 empty] | Vertical pipes | 9243.9614 | 12.9949 |  |  | Electricity
Radiation
[8 empty] | Emissivity | 0.8
[9 empty] | HTC, BTU/hr ft2 F | HTC, W/m2 C
[9 empty] | 639.8049 | 3632.94
[9 empty] | Heat loss BTU/ft | Heat loss kW/m
[9 empty] | 17092.0992 | 97.0524
[8 empty] | Insulated, kW | 6.6003
[8 empty] | Uninsulated, kW | 6405.8945