## Information
For compressed air systems, air leaking out of the system can account for up to 50% of the system demand. The reverse holds true for refrigeration systems, where air leaking in - termed infiltration - can account for a similar proportion of the system load.
The primary source of infiltration into a refrigerated room is through door openings. Similar to your refrigerator at home, repeated door opening results in the compressor coming on to remove the heat you have let in. In a commerical or industrial cold store or chiller, the logistics of product movement requires repeated access to the store by personnel either on foot or a forklift.
The heat loss calculator is designed to help identify opportunities for improvement. It is not intended as a detailed design tool and should not be used as such. If, by using the calculator, you are made aware of an area where improvements may yield savings in costs, energy and greenhouse gas emissions and this sparks further investigation, then the tool has been used appropriately. We would expect and recommend that, particularly where the scale of the capital expenditure and process changes required are signficant, that you seek competent expert assistance to confirm the value of any proposed changes.
The following calculators estimate the heat load on a refrigeration system resulting from a range of access door configurations There are a range of devices available to reduce door infiltration including plastic strip curtains, air curtains, sliding doors and fast acting roller doors. All have advantages and disadvantages and their suitability depends on local conditions, of which the door traffic frequency is a prime example.
It is not intended to compare all the various configurations, but rather to demonstrate the impact limiting the infiltration of warm air into your refrigeration store has on your energy consumption and cost.
The first input requirement is simply the basic door dimensions.
The calculator also requires you to input an estimate of the number of times people or a forklift enter the store (entered as the number of door openings or forklift entries per hour). The calculator assumes an average door opening duration of 60 seconds, reduced to 20 seconds where a strip curtain is installed. Daily operating hours and the days per year are entered and used, together with a mean electricty cost, to generate annual energy and cost savings data. Finally, the store temperature and the ambient temperature outside the door are entered.
The calculator compares an extreme base case where the door is permanently open with increasing degrees of protection.
l | The damaged strip curtain option is considered equivalent to a curtain with one strip missing (about 3 times the infiltration rate of a well maintained curtain), and the door permanently open during operating hours.
l | For the personnel door, it is assumed the door is only opened as necessary, that there is no additional strip curtain protection but that the door is well sealed when closed.
l | The permanently open door with a well maintained curtain is about 3 times more effective than the damaged curtain.
l | The addition of a sliding door together with a strip curtain completes the options considered for the forklift egress door.

## Infiltration small
Energy waste from refrigerated store personnel doors
[6 empty] | Average duration (seconds) | Door unprotected per hr | Door open per day |  |  |  | Patm | 100000 | Pa
Door dimensions |  |  |  |  | Permanently open without a strip curtain | 3600 | 1 | 16
Width, m | 1.2 |  |  |  | Permanently open with a damaged strip curtain | 20 | 0.14444 | 2.3111
Height, m | 2.6 |  |  |  | Permanently open with a well maintained strip curtain | 20 | 0.14444 | 2.3111 |  |  |  |  | RH | 0.75 |  | RH | 0.9
[5 empty] | Normally closed door with well maintained seals | 60 | 0.43333 | 6.9333 |  |  |  | T | Volume | Density | Enthalpy | Volume | Density | Enthalpy
Door open time | [11 empty] | -36 | 0.68004 | 1.4705 | -35.9728 | 0.68006 | 1.4705 | -35.9271
Door openings per hour | 26 | [7 empty] | RH | Density | Enthalpy | -35 | 0.68293 | 1.4643 | -34.9406 | 0.68296 | 1.4642 | -34.8896
Operating hours per day | 16 | [7 empty] | 0.75 | 1.194 | 35.5437 | -34 | 0.68583 | 1.4581 | -33.9055 | 0.68585 | 1.458 | -33.8486
Operating days per year | 220 | [7 empty] | 0.9 | 1.3873 | -20.9443 | -33 | 0.68873 | 1.452 | -32.8674 | 0.68875 | 1.4519 | -32.804
[12 empty] | -32 | 0.69163 | 1.4459 | -31.8259 | 0.69166 | 1.4458 | -31.7554
Temperatures | [9 empty] | 0.86065 |  | -31 | 0.69453 | 1.4398 | -30.7808 | 0.69456 | 1.4398 | -30.7023
Outside the door opening, C | 15 | [10 empty] | -30 | 0.69743 | 1.4338 | -29.7316 | 0.69747 | 1.4338 | -29.6444
Chiller/freezer, C | -22 | [10 empty] | -29 | 0.70033 | 1.4279 | -28.6779 | 0.70038 | 1.4278 | -28.5812
[12 empty] | -28 | 0.70324 | 1.422 | -27.6195 | 0.70329 | 1.4219 | -27.5122
Electricity cost, $/kWh | 0.1 | [10 empty] | -27 | 0.70615 | 1.4161 | -26.5558 | 0.7062 | 1.416 | -26.4369
[12 empty] | -26 | 0.70906 | 1.4103 | -25.4864 | 0.70912 | 1.4102 | -25.3548
[12 empty] | -25 | 0.71198 | 1.4045 | -24.4108 | 0.71204 | 1.4044 | -24.2651
| Daily energy waste, kWh/day | Daily energy waste cost, $/day | Annual energy waste cost, $/year | Incremental savings potential, $/year | [7 empty] | -24 | 0.71489 | 1.3988 | -23.3283 | 0.71497 | 1.3987 | -23.1673
Permanently open without a strip curtain (base case) | 1046.1005 | 104.6101 | 23014.2113 | [8 empty] | -23 | 0.71782 | 1.3931 | -22.2385 | 0.7179 | 1.393 | -22.0606
Permanently open with a damaged strip curtain | 330.1028 | 33.0103 | 7262.2622 | 15751.9491 |  |  |  |  | 1 |  |  | -22 | 0.72074 | 1.3875 | -21.1407 | 0.72083 | 1.3873 | -20.9443
Normally closed door with well maintained seals | 454.0302 | 45.403 | 9988.6645 | -2726.4023 |  |  |  |  | 2 |  |  | -21 | 0.72367 | 1.3818 | -20.0341 | 0.72377 | 1.3816 | -19.8175
Permanently open with a well maintained strip curtain | 203.4084 | 20.3408 | 4474.9855 | 5513.679 |  | Door always open no strip curtain |  |  | 3 |  |  | -20 | 0.72661 | 1.3763 | -18.918 | 0.72672 | 1.376 | -18.6794
Total savings potential over base case |  |  |  | 18539.2258 |  | Infiltration rate (l/s) | 1251.478 |  |  |  |  | -19 | 0.72955 | 1.3707 | -17.7917 | 0.72967 | 1.3705 | -17.5289
[6 empty] | Heat gain, kW | 98.0719 |  |  |  |  | -18 | 0.73249 | 1.3652 | -16.6543 | 0.73263 | 1.3649 | -16.365
[6 empty] | Assume COP 1.5, kWh/hr | 65.3813 |  |  |  |  | -17 | 0.73544 | 1.3597 | -15.5048 | 0.73559 | 1.3594 | -15.1866
[12 empty] | -16 | 0.7384 | 1.3543 | -14.3422 | 0.73857 | 1.354 | -13.9926
[6 empty] | Door always open plus damaged strip curtain | [5 empty] | -15 | 0.74136 | 1.3489 | -13.1655 | 0.74155 | 1.3485 | -12.7816
[6 empty] | With strip curtain (l/s) (door always open) | 214.1418 |  |  |  |  | -14 | 0.74434 | 1.3435 | -11.9735 | 0.74454 | 1.3431 | -11.5523
[6 empty] | Traffic effect/movement (l/s) | 180.769 |  |  |  |  | -13 | 0.74732 | 1.3381 | -10.7651 | 0.74754 | 1.3377 | -10.3031
[6 empty] | Total | 394.9108 |  |  |  |  | -12 | 0.75031 | 1.3328 | -9.5388 | 0.75056 | 1.3323 | -9.0326
[6 empty] | Heat gain, kW | 30.9471 |  |  |  |  | -11 | 0.75331 | 1.3275 | -8.2933 | 0.75358 | 1.327 | -7.7389
[6 empty] | Assume COP 1.5, kWh/hr | 20.6314 |  |  |  |  | -10 | 0.75632 | 1.3222 | -7.0271 | 0.75662 | 1.3217 | -6.4203
[12 empty] | -9 | 0.75934 | 1.3169 | -5.7385 | 0.75967 | 1.3164 | -5.0749
[6 empty] | Door always open plus well maintained strip curtain | [5 empty] | -8 | 0.76238 | 1.3117 | -4.4258 | 0.76274 | 1.3111 | -3.7005
[6 empty] | With strip curtain (l/s) (door always open) | 62.5739 |  |  |  |  | -7 | 0.76543 | 1.3065 | -3.0872 | 0.76582 | 1.3058 | -2.295
[6 empty] | Traffic effect/movement (l/s) | 180.769 |  |  |  |  | -6 | 0.76849 | 1.3012 | -1.7208 | 0.76892 | 1.3005 | -0.85593
[6 empty] | Total | 243.3429 |  |  |  |  | -5 | 0.77157 | 1.2961 | -0.32428 | 0.77204 | 1.2953 | 0.61922
[6 empty] | Heat gain, kW | 19.0695 |  |  |  |  | -4 | 0.77467 | 1.2909 | 1.1044 | 0.77518 | 1.29 | 2.1332
[6 empty] | Assume COP 1.5, kWh/hr | 12.713 |  |  |  |  | -3 | 0.77778 | 1.2857 | 2.5678 | 0.77834 | 1.2848 | 3.6888
[12 empty] | -2 | 0.78092 | 1.2805 | 4.0684 | 0.78153 | 1.2795 | 5.2892
[12 empty] | -1 | 0.78407 | 1.2754 | 5.6089 | 0.78474 | 1.2743 | 6.9377
[6 empty] | Normally closed door with good seals (no strip curtain) | [5 empty] | 0 | 0.78725 | 1.2702 | 7.1917 | 0.78798 | 1.2691 | 8.637
[6 empty] | Seal leakage (@0.1 l/s.m) | 0.86133 |  |  |  |  | 1 | 0.79042 | 1.2652 | 8.7459 | 0.7912 | 1.2639 | 10.3022
[6 empty] | Traffic effect/movement (l/s) | 542.3071 |  |  |  |  | 2 | 0.7936 | 1.2601 | 10.3365 | 0.79445 | 1.2587 | 12.0111
[6 empty] | Total | 543.1685 |  |  |  |  | 3 | 0.79681 | 1.255 | 11.9662 | 0.79773 | 1.2536 | 13.7673
[6 empty] | Heat gain, kW | 42.5653 |  |  |  |  | 4 | 0.80004 | 1.2499 | 13.6375 | 0.80103 | 1.2484 | 15.5735
[6 empty] | Assume COP 1.5, kWh/hr | 28.3769 |  |  |  |  | 5 | 0.8033 | 1.2449 | 15.3527 | 0.80436 | 1.2432 | 17.4327
[12 empty] | 6 | 0.80658 | 1.2398 | 17.1143 | 0.80772 | 1.2381 | 19.3479
[12 empty] | 7 | 0.80988 | 1.2347 | 18.9251 | 0.81111 | 1.2329 | 21.3223
[12 empty] | 8 | 0.81322 | 1.2297 | 20.7877 | 0.81454 | 1.2277 | 23.3595
[12 empty] | 9 | 0.81659 | 1.2246 | 22.7051 | 0.81801 | 1.2225 | 25.4628
[12 empty] | 10 | 0.81999 | 1.2195 | 24.6804 | 0.82152 | 1.2173 | 27.6361
[12 empty] | 11 | 0.82342 | 1.2144 | 26.7168 | 0.82506 | 1.212 | 29.8833
[12 empty] | 12 | 0.82689 | 1.2093 | 28.8177 | 0.82866 | 1.2068 | 32.2085
[12 empty] | 13 | 0.8304 | 1.2042 | 30.9867 | 0.83229 | 1.2015 | 34.616
[12 empty] | 14 | 0.83395 | 1.1991 | 33.2273 | 0.83598 | 1.1962 | 37.1105
[12 empty] | 15 | 0.83754 | 1.194 | 35.5437 | 0.83972 | 1.1909 | 39.6967
[12 empty] | 16 | 0.84118 | 1.1888 | 37.9398 | 0.84352 | 1.1855 | 42.3796
[12 empty] | 17 | 0.84487 | 1.1836 | 40.4199 | 0.84737 | 1.1801 | 45.1645
[12 empty] | 18 | 0.84861 | 1.1784 | 42.9886 | 0.85128 | 1.1747 | 48.0569
[12 empty] | 19 | 0.8524 | 1.1732 | 45.6505 | 0.85527 | 1.1692 | 51.0627
[12 empty] | 20 | 0.85625 | 1.1679 | 48.4106 | 0.85931 | 1.1637 | 54.1881
[12 empty] | 21 | 0.86015 | 1.1626 | 51.2742 | 0.86344 | 1.1582 | 57.4394
[12 empty] | 22 | 0.86412 | 1.1572 | 54.2466 | 0.86764 | 1.1526 | 60.8234
[12 empty] | 23 | 0.86816 | 1.1519 | 57.3336 | 0.87192 | 1.1469 | 64.3472
[12 empty] | 24 | 0.87227 | 1.1464 | 60.5412 | 0.87629 | 1.1412 | 68.0184
[12 empty] | 25 | 0.87645 | 1.141 | 63.8757 | 0.88074 | 1.1354 | 71.8447
[12 empty] | 26 | 0.88072 | 1.1354 | 67.3438 | 0.8853 | 1.1296 | 75.8345
[12 empty] | 27 | 0.88506 | 1.1299 | 70.9523 | 0.88995 | 1.1237 | 79.9966
[12 empty] | 28 | 0.88949 | 1.1242 | 74.7086 | 0.89471 | 1.1177 | 84.3401
[12 empty] | 29 | 0.89401 | 1.1186 | 78.6204 | 0.89959 | 1.1116 | 88.8747
[12 empty] | 30 | 0.89864 | 1.1128 | 82.6957 | 0.90459 | 1.1055 | 93.6107
[12 empty] | 31 | 0.90336 | 1.107 | 86.943 | 0.90971 | 1.0993 | 98.5588
[12 empty] | 32 | 0.90819 | 1.1011 | 91.3713 | 0.91496 | 1.0929 | 103.7304
[12 empty] | 33 | 0.91313 | 1.0951 | 95.99 | 0.92036 | 1.0865 | 109.1376
[12 empty] | 34 | 0.9182 | 1.0891 | 100.809 | 0.9259 | 1.08 | 114.793
[12 empty] | 35 | 0.92339 | 1.083 | 105.8388 | 0.9316 | 1.0734 | 120.7102
[12 empty] | 36 | 0.92872 | 1.0768 | 111.0903 | 0.93747 | 1.0667 | 126.9033

## Infiltration large
Energy waste from refrigerated store forklift doors
[6 empty] | Average duration (seconds) | Door unprotected per hr | Door open per day |  |  |  | Patm | 100000 | Pa
Door dimensions |  |  |  |  | Permanently open without a strip curtain | 3600 | 1 | 16
Width, m | 0.9 |  |  |  | Permanently open with a damaged strip curtain | 20 | 0.13889 | 2.2222
Height, m | 3.2 |  |  |  | Permanently open with a well maintained strip curtain | 20 | 0.13889 | 2.2222 |  |  |  |  | RH | 0.75 |  | RH | 0.9
[5 empty] | Sliding door plus a well maintained strip curtain | 60 | 0.41667 | 6.6667 |  |  |  | T | Volume | Density | Enthalpy | Volume | Density | Enthalpy
Door open time | [11 empty] | -36 | 0.68004 | 1.4705 | -35.9728 | 0.68006 | 1.4705 | -35.9271
Forklift movements per hour | 25 | [7 empty] | RH | Density | Enthalpy | -35 | 0.68293 | 1.4643 | -34.9406 | 0.68296 | 1.4642 | -34.8896
Operating hours per day | 16 | [7 empty] | 0.75 | 1.194 | 35.5437 | -34 | 0.68583 | 1.4581 | -33.9055 | 0.68585 | 1.458 | -33.8486
Operating days per year | 210 | [7 empty] | 0.9 | 1.2484 | 15.5735 | -33 | 0.68873 | 1.452 | -32.8674 | 0.68875 | 1.4519 | -32.804
[12 empty] | -32 | 0.69163 | 1.4459 | -31.8259 | 0.69166 | 1.4458 | -31.7554
Temperatures | [9 empty] | 0.9564 |  | -31 | 0.69453 | 1.4398 | -30.7808 | 0.69456 | 1.4398 | -30.7023
Outside the door opening, C | 15 | [10 empty] | -30 | 0.69743 | 1.4338 | -29.7316 | 0.69747 | 1.4338 | -29.6444
Chiller/freezer, C | 4 | [10 empty] | -29 | 0.70033 | 1.4279 | -28.6779 | 0.70038 | 1.4278 | -28.5812
[12 empty] | -28 | 0.70324 | 1.422 | -27.6195 | 0.70329 | 1.4219 | -27.5122
Electricity cost, $/kWh | 0.1 | [10 empty] | -27 | 0.70615 | 1.4161 | -26.5558 | 0.7062 | 1.416 | -26.4369
[6 empty] | 2 | [5 empty] | -26 | 0.70906 | 1.4103 | -25.4864 | 0.70912 | 1.4102 | -25.3548
[12 empty] | -25 | 0.71198 | 1.4045 | -24.4108 | 0.71204 | 1.4044 | -24.2651
| Daily energy waste, kWh/day | Daily energy waste cost, $/day | Annual energy waste cost, $/year | Incremental savings potential, $/year | [7 empty] | -24 | 0.71489 | 1.3988 | -23.3283 | 0.71497 | 1.3987 | -23.1673
Permanently open without a strip curtain (base case) | 195.8141 | 19.5814 | 4112.0965 | [8 empty] | -23 | 0.71782 | 1.3931 | -22.2385 | 0.7179 | 1.393 | -22.0606
Permanently open with a damaged strip curtain | 44.6574 | 4.4657 | 937.8045 | 3174.292 |  |  |  |  | 1 |  |  | -22 | 0.72074 | 1.3875 | -21.1407 | 0.72083 | 1.3873 | -20.9443
Permanently open with a well maintained strip curtain | 19.3647 | 1.9365 | 406.6587 | 531.1458 |  |  |  |  | 2 |  |  | -21 | 0.72367 | 1.3818 | -20.0341 | 0.72377 | 1.3816 | -19.8175
Sliding door plus a well maintained strip curtain | 16.4973 | 1.6497 | 346.4433 | 60.2154 |  | Door always open no strip curtain |  |  | 3 |  |  | -20 | 0.72661 | 1.3763 | -18.918 | 0.72672 | 1.376 | -18.6794
Total savings potential over base case |  |  |  | 3765.6531 |  | Infiltration rate (l/s) | 736.3429 |  |  |  |  | -19 | 0.72955 | 1.3707 | -17.7917 | 0.72967 | 1.3705 | -17.5289
[6 empty] | Heat gain, kW | 18.3576 |  |  |  |  | -18 | 0.73249 | 1.3652 | -16.6543 | 0.73263 | 1.3649 | -16.365
[6 empty] | Assume COP 1.5, kWh/hr | 12.2384 |  |  |  |  | -17 | 0.73544 | 1.3597 | -15.5048 | 0.73559 | 1.3594 | -15.1866
[12 empty] | -16 | 0.7384 | 1.3543 | -14.3422 | 0.73857 | 1.354 | -13.9926
[6 empty] | Door always open plus damaged strip curtain | [5 empty] | -15 | 0.74136 | 1.3489 | -13.1655 | 0.74155 | 1.3485 | -12.7816
[6 empty] | With strip curtain (l/s) (door always open) | 126.8146 |  |  |  |  | -14 | 0.74434 | 1.3435 | -11.9735 | 0.74454 | 1.3431 | -11.5523
[6 empty] | Forklift effect/movement (l/s) | 41.1157 |  |  |  |  | -13 | 0.74732 | 1.3381 | -10.7651 | 0.74754 | 1.3377 | -10.3031
[6 empty] | Total | 167.9303 |  |  |  |  | -12 | 0.75031 | 1.3328 | -9.5388 | 0.75056 | 1.3323 | -9.0326
[6 empty] | Heat gain, kW | 4.1866 |  |  |  |  | -11 | 0.75331 | 1.3275 | -8.2933 | 0.75358 | 1.327 | -7.7389
[6 empty] | Assume COP 1.5, kWh/hr | 2.7911 |  |  |  |  | -10 | 0.75632 | 1.3222 | -7.0271 | 0.75662 | 1.3217 | -6.4203
[12 empty] | -9 | 0.75934 | 1.3169 | -5.7385 | 0.75967 | 1.3164 | -5.0749
[6 empty] | Door always open plus well maintained strip curtain | [5 empty] | -8 | 0.76238 | 1.3117 | -4.4258 | 0.76274 | 1.3111 | -3.7005
[6 empty] | With strip curtain (l/s) (door always open) | 31.7037 |  |  |  |  | -7 | 0.76543 | 1.3065 | -3.0872 | 0.76582 | 1.3058 | -2.295
[6 empty] | Forklift effect/movement (l/s) | 41.1157 |  |  |  |  | -6 | 0.76849 | 1.3012 | -1.7208 | 0.76892 | 1.3005 | -0.85593
[6 empty] | Total | 72.8194 |  |  |  |  | -5 | 0.77157 | 1.2961 | -0.32428 | 0.77204 | 1.2953 | 0.61922
[6 empty] | Heat gain, kW | 1.8154 |  |  |  |  | -4 | 0.77467 | 1.2909 | 1.1044 | 0.77518 | 1.29 | 2.1332
[6 empty] | Assume COP 1.5, kWh/hr | 1.2103 |  |  |  |  | -3 | 0.77778 | 1.2857 | 2.5678 | 0.77834 | 1.2848 | 3.6888
[12 empty] | -2 | 0.78092 | 1.2805 | 4.0684 | 0.78153 | 1.2795 | 5.2892
[12 empty] | -1 | 0.78407 | 1.2754 | 5.6089 | 0.78474 | 1.2743 | 6.9377
[6 empty] | Activated sliding door plus strip curtain | [5 empty] | 0 | 0.78725 | 1.2702 | 7.1917 | 0.78798 | 1.2691 | 8.637
[6 empty] | Seal leakage (@01 l/s.m) | 5.5806 |  |  |  |  | 1 | 0.79042 | 1.2652 | 8.7459 | 0.7912 | 1.2639 | 10.3022
[6 empty] | Door open with strip curtain | 15.3405 |  |  |  |  | 2 | 0.7936 | 1.2601 | 10.3365 | 0.79445 | 1.2587 | 12.0111
[6 empty] | Forklift effect/movement (l/s) | 41.1157 |  |  |  |  | 3 | 0.79681 | 1.255 | 11.9662 | 0.79773 | 1.2536 | 13.7673
[6 empty] | Total | 62.0368 |  |  |  |  | 4 | 0.80004 | 1.2499 | 13.6375 | 0.80103 | 1.2484 | 15.5735
[6 empty] | Heat gain, kW | 1.5466 |  |  |  |  | 5 | 0.8033 | 1.2449 | 15.3527 | 0.80436 | 1.2432 | 17.4327
[6 empty] | Assume COP 1.5, kWh/hr | 1.0311 |  |  |  |  | 6 | 0.80658 | 1.2398 | 17.1143 | 0.80772 | 1.2381 | 19.3479
[12 empty] | 7 | 0.80988 | 1.2347 | 18.9251 | 0.81111 | 1.2329 | 21.3223
[12 empty] | 8 | 0.81322 | 1.2297 | 20.7877 | 0.81454 | 1.2277 | 23.3595
[12 empty] | 9 | 0.81659 | 1.2246 | 22.7051 | 0.81801 | 1.2225 | 25.4628
[12 empty] | 10 | 0.81999 | 1.2195 | 24.6804 | 0.82152 | 1.2173 | 27.6361
[12 empty] | 11 | 0.82342 | 1.2144 | 26.7168 | 0.82506 | 1.212 | 29.8833
[12 empty] | 12 | 0.82689 | 1.2093 | 28.8177 | 0.82866 | 1.2068 | 32.2085
[12 empty] | 13 | 0.8304 | 1.2042 | 30.9867 | 0.83229 | 1.2015 | 34.616
[12 empty] | 14 | 0.83395 | 1.1991 | 33.2273 | 0.83598 | 1.1962 | 37.1105
[12 empty] | 15 | 0.83754 | 1.194 | 35.5437 | 0.83972 | 1.1909 | 39.6967
[12 empty] | 16 | 0.84118 | 1.1888 | 37.9398 | 0.84352 | 1.1855 | 42.3796
[12 empty] | 17 | 0.84487 | 1.1836 | 40.4199 | 0.84737 | 1.1801 | 45.1645
[12 empty] | 18 | 0.84861 | 1.1784 | 42.9886 | 0.85128 | 1.1747 | 48.0569
[12 empty] | 19 | 0.8524 | 1.1732 | 45.6505 | 0.85527 | 1.1692 | 51.0627
[12 empty] | 20 | 0.85625 | 1.1679 | 48.4106 | 0.85931 | 1.1637 | 54.1881
[12 empty] | 21 | 0.86015 | 1.1626 | 51.2742 | 0.86344 | 1.1582 | 57.4394
[12 empty] | 22 | 0.86412 | 1.1572 | 54.2466 | 0.86764 | 1.1526 | 60.8234
[12 empty] | 23 | 0.86816 | 1.1519 | 57.3336 | 0.87192 | 1.1469 | 64.3472
[12 empty] | 24 | 0.87227 | 1.1464 | 60.5412 | 0.87629 | 1.1412 | 68.0184
[12 empty] | 25 | 0.87645 | 1.141 | 63.8757 | 0.88074 | 1.1354 | 71.8447
[12 empty] | 26 | 0.88072 | 1.1354 | 67.3438 | 0.8853 | 1.1296 | 75.8345
[12 empty] | 27 | 0.88506 | 1.1299 | 70.9523 | 0.88995 | 1.1237 | 79.9966
[12 empty] | 28 | 0.88949 | 1.1242 | 74.7086 | 0.89471 | 1.1177 | 84.3401
[12 empty] | 29 | 0.89401 | 1.1186 | 78.6204 | 0.89959 | 1.1116 | 88.8747
[12 empty] | 30 | 0.89864 | 1.1128 | 82.6957 | 0.90459 | 1.1055 | 93.6107
[12 empty] | 31 | 0.90336 | 1.107 | 86.943 | 0.90971 | 1.0993 | 98.5588
[12 empty] | 32 | 0.90819 | 1.1011 | 91.3713 | 0.91496 | 1.0929 | 103.7304
[12 empty] | 33 | 0.91313 | 1.0951 | 95.99 | 0.92036 | 1.0865 | 109.1376
[12 empty] | 34 | 0.9182 | 1.0891 | 100.809 | 0.9259 | 1.08 | 114.793
[12 empty] | 35 | 0.92339 | 1.083 | 105.8388 | 0.9316 | 1.0734 | 120.7102
[12 empty] | 36 | 0.92872 | 1.0768 | 111.0903 | 0.93747 | 1.0667 | 126.9033