## Lighting Information
Lighting offers a significant opportunity for electrical energy savings. Lamp efficiency continues to improve and there are also many control options that can enhance potential savings.
The following calculator helps compare (up to 5) different lamp options and is intended as a tool to assist you identify more efficient and cost effective lighting options. It is not a design tool and should be used as such.
The tool provides drop-down menus for lamp type and corresponding lamp watt rating. Lamps, watts and the area illuminated can be entered for up to 5 different options. For a straight comparison between lamps, keep the area the same - to calculate the energy requirements of a mix of lamps, enter the respective floor (or work surface) area as required.
For an entered number of lamps, the calculator automatically calculates the total installed light intensity (measured in lumens) and the average illuminance (or lighting level), measured in lux, which is simply the light intensity divided by the area being illuminated. The installed power and the power per unit area is also calculated.
Although power requirements will vary with the application, in an office situation for example, targeting an energy intensity less than 10 W/m2 should be considered.
Entering an average electricity cost and annual operating hours allows comparison of annual running cost of the selected lamp options.
NOTE: It is important to note that the average illuminance should not be used as the sole design criteria as the calculator accounts for neither the height of the lamp(s) above the working surface nor the distribution of the lamps. Because light follows an inverse square law, the illuminance 4 metres below a lamp, for example, is only 1/16 of the illuminance 1 metre below the lamp. Good design is necessary to achieve both effective and energy efficient lighting.

## Lighting calculator
Lighting Option Comparison
[14 empty] | Lamp reference | Lamp type | Watt ref | Watt | Lumens/W | Typical lamp life | Operating cost
Lighting option | Illuminated area (m2) | Lamp Type | Lamp Rating (W) | No. of Lamps | Total load (W) | Total light intensity (lumens) | Average illuminance (lux, or lm/m2) | Power density, W/m2 | Typical lamp life | 2 | 7 | 2 | Case 1 | 6 | Sodium: Low pressure | 5 | 135 | 159 | Good/very good | Very low
1 | 320 |  |  | 100 | 16200 | 2575800 | 8049.375 | 50.625 | Good/very good | 3 | 4 | 3 | Case 2 | 4 | Metal halide: pulse start | 1 | 250 | 94 | Very good | Low
2 | 320 |  |  | 14 | 4060 | 381640 | 1192.625 | 12.6875 | Very good | 11 | 8 | 11 | Case 3 | 5 | Sodium: High pressure | 6 | 250 | 118 | Excellent | Very low
3 | 320 |  |  | 11 | 3080 | 363440 | 1135.75 | 9.625 | Excellent | 9 | 4 | 9 | Case 4 | 9 | Fluorescent T5 | 2 | 21 | 100 | Good | Low
4 | 320 |  |  | 100 | 2100 | 210000 | 656.25 | 6.5625 | Good | 6 | 6 | 6 | Case 5 | 5 | Sodium: High pressure | 4 | 100 | 95 | Excellent | Very low
5 | 320 |  |  | 100 | 11200 | 1064000 | 3325 | 35 | Excellent
[13 empty] | Lamp ref | Lamp type | Typical lamp life | Operating cost
Annual operating cost | [12 empty] | 1 | Incandescent | Low | High
[13 empty] | 2 | Mercury vapour | Very good | Moderate
Average electricity cost, $/kWh |  | 0.1 | per kWh | [9 empty] | 3 | Metal halide: standard | Very good | Low/moderate
Annual operating hours |  | 5500 | hrs | [9 empty] | 4 | Metal halide: pulse start | Very good | Low
[13 empty] | 5 | Sodium: High pressure | Excellent | Very low
Lighting options | Estimated annual energy cost, $/yr | [11 empty] | 6 | Sodium: Low pressure | Good/very good | Very low
1 | 8910 | [11 empty] | 7 | Fluorescent T12 | Low/moderate | Moderate
2 | 2233 | [11 empty] | 8 | Fluorescent T8 | Good | Low
3 | 1694 | [11 empty] | 9 | Fluorescent T5 | Good | Low
4 | 1155 | [11 empty] | 10 | Fluorescent T5 High output | Good | Low
5 | 6160 | [11 empty] | 11 | Compact fluorescent | Moderate | Low
http://www.eere.energy.gov/consumer/your_home/lighting_daylighting/index.cfm/mytopic=12030
Scenarios
0
[5 empty] | 0 | [7 empty] | Watt ref | Lamp Watt | Case 1 | Lamp Watt | Case 2 | Lamp Watt | Case 3 | Lamp Watt | Case 4 | Lamp Watt | Case 5
[5 empty] | 0 | [7 empty] | 1 | 18 | 100 | 250 | 94 | 35 | 51 | 14 | 96 | 35 | 51
[13 empty] | 2 | 35 | 129 | 320 | 100 | 50 | 72 | 21 | 100 | 50 | 72
[13 empty] | 3 | 55 | 134 | 400 | 105 | 70 | 86 | 28 | 104 | 70 | 86
[13 empty] | 4 | 90 | 144 | 750 | 100 | 100 | 95 | 35 | 104 | 100 | 95
[13 empty] | 5 | 135 | 159 | 1000 | 100 | 150 | 103 | 0 | 0 | 150 | 103
[13 empty] | 6 | 180 | 183 | 0 | 0 | 250 | 118 | 0 | 0 | 250 | 118
[13 empty] | 7 | 0 | 0 | 0 | 0 | 400 | 128 | 0 | 0 | 400 | 128
[13 empty] | 8 | 0 | 0 | 0 | 0 | 600 | 150 | 0 | 0 | 600 | 150
[13 empty] | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[13 empty] | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Incandescent
25 | 9
40 | 10
60 | 12
75 | 12
100 | 13
200 | 15
500 | 16
1000 | 18
Mercury vapour
50 | 36
80 | 48
100 | 50
125 | 50
150 | 79
175 | 48
250 | 52
400 | 55
500 | 55
700 | 57
1000 | 60
Metal halide: standard
70 | 73
100 | 85
150 | 87
250 | 73
400 | 100
1000 | 115
Metal halide: pulse start
250 | 94
320 | 100
400 | 105
750 | 100
1000 | 100
Sodium: High pressure
35 | 51
50 | 72
70 | 86
100 | 95
150 | 103
250 | 118
400 | 128
600 | 150
Sodium: Low pressure
18 | 100
35 | 129
55 | 134
90 | 144
135 | 159
180 | 183
Fluorescent T12
40 | 66
52 | 75
55 | 75
58 | 49
60 | 88
75 | 80
Fluorescent T8
18 | 75
36 | 93
58 | 90
70 | 86
Fluorescent T5
14 | 96
21 | 100
28 | 104
35 | 104
Fluorescent T5HO
24 | 83
39 | 90
49 | 100
54 | 93
Compact fluorescent
5 | 50
7 | 60
9 | 54
11 | 54
15 | 60
18 | 60
20 | 60
26 | 69
32 | 75
42 | 76